## STM_existing_old (hidden)
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS | Optimally Sized Gen | STM WITH EXISTING PV | STM Baseline | 1 Hr | 3 Hr | 10 Hr | 24 Hr
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 100 | NPV | 406512 | -1951517 | -2618918 | -11295829 | -29634101
LCC | 60450030 | 60085900 | 60124300 | 60827400 |  | Microgrid_Premium_Pct | Default (0.30) | PV Rated Capacity [kW] | 3830.7049 | 3776.5918 | 3907.4017 | 4289.3379 | 7505.7646
PV Rated Capacity [kW] | 3580.54 | 3580.54 | 3626.6286 | 3746.5719 |  | Gen_min_turndown_pct | 0 | Battery Storage Capacity [kWh] | 675.6722 | 1887.399 | 1879.9992 | 17951.7657 | 42079.4774
Battery Rated Power [kW] | 718.7755 | 668.78 | 484.619 | 534.199 |  | Generator allowed? | YES | Battery Rated Power [kW] | 325.5633 | 1013.8258 | 622.4096 | 1846.7016 | 4112.2006
Battery Storage Capacity [kWh] | 1200.2803 | 1367.52 | 1033.7 | 1010.61 |  | Generator_existing_kw | 0 | Generator Rated Power [kW] | 0 | 1135.01 | 1804.44 | 867.763 | 433.553
Generator Rated Power [kW] | 2043.7245 | 1882.45 | 2036.28 | 2387.38 |  |  |  | Initial Capital Cost | 957519.34 | 2525509.13 | 2737622.45 | 10658929.08 | 27624764.87
Net Capital Cost (plus O&M) | 6336317 | 6142657 | 5966364 | 6874904 |  |  |  | Net Capital Cost (plus O&M) | 2915736 | 6455919 | 7239810 | 20856749 | 50430082
Expected Outage Cost | 0 | 0 | 0 | 0 |  |  |  | Energy Savings (Year One) | 12028 | 9175.84 | 15508.06 | 30487.75 | 178221.01
Max Outage Cost | 0 | 0 | 0 | 0 |  |  |  | Demand Savings (Year One) | 78655.81 | 133115.09 | 131868.25 | 332546.38 | 675281.67
Year One Bill (Total Utility Cost) | 2301494.16 | 2296140 | 2309850 | 2294150
MicroGrid Upgrade Costs | 1395007.0124 | 1347437.644 | 1247781.9308 | 1401820.245
Total Unserved Load | 0 | 0 | 0 | 0
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS | 100% Renewable
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 100
LCC | 65334748 | 65391606 | 65644687 | 67009566 |  | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | 3727.6945 | 3627.091 | 3580.54 | 3580.54 |  | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | 652.2792 | 684.1302 | 582.2773 | 1120.3543 |  | Generator allowed? | NO
Battery Storage Capacity [kWh] | 2569.0791 | 2602.5484 | 1886.2258 | 3549.9104 |  | Generator_existing_kw | n/a
Generator Rated Power [kW] | 0 | 0 | 0 | 0
Net Capital Cost (plus O&M) | 4567997 | 4373817 | 3554075 | 5627940
Expected Outage Cost | 8213063.3441 | 8191260.8714 | 8657885.5369 | 7887647.0091
Max Outage Cost | 8213063.3441 | 8191260.8714 | 8657885.5369 | 7887647.0091
Year One Bill (Total Utility Cost) | 2255954.07 | 2266902.47 | 2302452.56 | 2278035.49
MicroGrid Upgrade Costs | 879380.6469 | 901474.5597 | 692730.4308 | 1314889.9628
Total Unserved Load | 42146.6652 | 189523.2052 | 1375248.4991 | 27256475.7816
STM EXISTING PV 100% RENEWABLE | VoLL
2 HOUR OUTAGE DURATION - 8760 | 10 | 29 | 40 | 70 | 100 | 180 | 213
LCC | 57041811 | 59515685 | 60787540 | 64078190 | 67009566 | 71370501 | 71489323
PV Rated Capacity [kW] | 3832.8957 | 3832.8957 | 3848.9787 | 3640.8564 | 3580.54 | 3785.4099 | 3798.7031
Battery Rated Power [kW] | 338.9311 | 338.9311 | 345.3439 | 550.861 | 1120.3543 | 2762.5 | 2921.575
Battery Storage Capacity [kWh] | 732.0735 | 732.0735 | 903.9912 | 1495.2216 | 3549.9104 | 15098.9769 | 15658.3572
Generator Rated Power [kW] | 0 | 0 | 0 | 0 | 0 | 0 | 0
Net Capital Cost (plus O&M) | 2984475 | 2984475 | 3166908 | 3371554 | 5627940 | 17391753 | 18091272
Expected Outage Cost | 1302039.1237 | 3775913.4587 | 4580022.9982 | 7347689.8356 | 7887647.0091 | 655901.5715 | 0
Max Outage Cost | 1302039.1237 | 3775913.4587 | 4580022.9982 | 7347689.8356 | 7887647.0091 | 655901.5715 | 0
Year One Bill (Total Utility Cost) | 2303072.32 | 2303072.32 | 2299723.47 | 2303708.77 | 2278035.49 | 2124058.24 | 2118662.63
MicroGrid Upgrade Costs | 0 | 0 | 362189.3176 | 589801.7198 | 1314889.9628 | 4680412.3981 | 4879651.5716
Total Unserved Load | 35831622.81 | 35831622.81 | 34935557.2967 | 34380481.7365 | 27256475.7816 | 1377040.235 | 0
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS | Existing Generator
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 100
LCC | 60346334 | 59982206 | 60020615 | 60723698 |  | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | 3580.54 | 3580.54 | 3626.6286 | 3746.5719 |  | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | 718.7755 | 668.7799 | 484.6192 | 534.1989 |  | Generator allowed? | NO
Battery Storage Capacity [kWh] | 1200.2803 | 1367.519 | 1033.7015 | 1010.6089 |  | Generator_existing_kw | n/a
Generator Rated Power [kW] | 2043.7245 | 1882.4484 | 2036.277 | 2387.3761
Net Capital Cost (plus O&M) | 6232621 | 6038962 | 5862668 | 6771208
Expected Outage Cost | 0 | 0 | 0 | 0
Max Outage Cost | 0 | 0 | 0 | 0
Year One Bill (Total Utility Cost) | 2301494.16 | 2296135.62 | 2309845.68 | 2294150.71
MicroGrid Upgrade Costs | 1395007.0124 | 1347437.644 | 1247781.9308 | 1401820.245
Total Unserved Load | 0 | 0 | 0 | 0
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 50
LCC | [5 empty] | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | [5 empty] | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | [5 empty] | Generator allowed? | YES
Battery Storage Capacity [kWh] | [5 empty] | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 150
LCC | [5 empty] | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | [5 empty] | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | [5 empty] | Generator allowed? | YES
Battery Storage Capacity [kWh] | [5 empty] | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 100
LCC | [5 empty] | Microgrid_Premium_Pct | 0.15
PV Rated Capacity [kW] | [5 empty] | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | [5 empty] | Generator allowed? | YES
Battery Storage Capacity [kWh] | [5 empty] | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 100
LCC | [5 empty] | Microgrid_Premium_Pct | 0.5
PV Rated Capacity [kW] | [5 empty] | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | [5 empty] | Generator allowed? | YES
Battery Storage Capacity [kWh] | [5 empty] | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV | # Outage Start Timesteps |  |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 |  | VoLL | 100
LCC | [5 empty] | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | [5 empty] | Gen_min_turndown_pct | 0.25
Battery Rated Power [kW] | [5 empty] | Generator allowed? | YES
Battery Storage Capacity [kWh] | [5 empty] | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load

## STM_existing_sseb_crit_old (hidden)
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS | Optimally Sized Gen | STM WITH EXISTING PV | STM Baseline | 1 Hr | 3 Hr | 10 Hr | 24 Hr
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 100 | NPV | 406512 | -1951517 | -2618918 | -11295829 | -29634101
LCC | 55772516 | 55750300 | 55750700 | 55785300 | Microgrid_Premium_Pct | Default (0.30) | PV Rated Capacity [kW] | 3830.7049 | 3776.5918 | 3907.4017 | 4289.3379 | 7505.7646
PV Rated Capacity [kW] | 3832.8957 | 3832.8957 | 3832.8957 | 3832.8957 | Gen_min_turndown_pct | 0 | Battery Storage Capacity [kWh] | 675.6722 | 1887.399 | 1879.9992 | 17951.7657 | 42079.4774
Battery Rated Power [kW] | 338.931 | 338.931 | 338.931 | 338.931 | Generator allowed? | YES | Battery Rated Power [kW] | 325.5633 | 1013.8258 | 622.4096 | 1846.7016 | 4112.2006
Battery Storage Capacity [kWh] | 732.074 | 732.074 | 732.074 | 732.074 | Generator_existing_kw | 0 | Generator Rated Power [kW] | 0 | 1135.01 | 1804.44 | 867.763 | 433.553
Generator Rated Power [kW] | 17.2082 | 5.5487 | 5.72 | 23.9272 |  |  | Initial Capital Cost | 957519.34 | 2525509.13 | 2737622.45 | 10658929.08 | 27624764.87
Net Capital Cost (plus O&M) | 3010520 | 2992873 | 2993133 | 3020690 |  |  | Net Capital Cost (plus O&M) | 2915736 | 6455919 | 7239810 | 20856749 | 50430082
Expected Outage Cost | 0 | 0 | 0 | 0 |  |  | Energy Savings (Year One) | 12028 | 9175.84 | 15508.06 | 30487.75 | 178221.01
Max Outage Cost | 0 | 0 | 0 | 0 |  |  | Demand Savings (Year One) | 78655.81 | 133115.09 | 131868.25 | 332546.38 | 675281.67
Year One Bill (Total Utility Cost) | 2303070 | 2303070 | 2303070 | 2303070
MicroGrid Upgrade Costs | 6699.2598 | 2159.95 | 2226.84 | 9314.89
Total Unserved Load | 0 | 0 | 0 | 0
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS | 100% Renewable
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 100
LCC | 55817022 | 55762842 | 55765500 | 55845949 | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | 3832.8957 | 3832.8957 | 3832.9 | 3832.8957 | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | 338.9311 | 338.9311 | 338.931 | 338.9311 | Generator allowed? | NO
Battery Storage Capacity [kWh] | 732.0735 | 732.0735 | 732.074 | 732.0735 | Generator_existing_kw | n/a
Generator Rated Power [kW] | 0 | 0 | 0 | 0
Net Capital Cost (plus O&M) | 2984475 | 2984475 | 2984475 | 2984475
Expected Outage Cost | 77249.9423 | 23070.207 | 25764 | 106177.0949
Max Outage Cost | 77249.9423 | 23070.207 | 25764.0226 | 106177.0949
Year One Bill (Total Utility Cost) | 2303072.32 | 2303072.32 | 2303070 | 2303072.32
MicroGrid Upgrade Costs | 0 | 0 | 0 | 0
Total Unserved Load | 202.2565 | 465.5327 | 3205.51 | 153071.5228
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS | Existing Generator
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 100
LCC | 55788273 | 55780227 | 55782900 | 55788276 | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | 3832.8957 | 3832.8957 | 3832.8957 | 3832.8957 | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | 338.9311 | 338.9311 | 338.9311 | 338.9311 | Generator allowed? | NO
Battery Storage Capacity [kWh] | 732.0735 | 732.0735 | 732.074 | 732.0735 | Generator_existing_kw | n/a
Generator Rated Power [kW] | 80 | 80 | 80 | 80
Net Capital Cost (plus O&M) | 3001861 | 3001861 | 3001861 | 3001861
Expected Outage Cost | 0 | 23070.207 | 25764 | 0
Max Outage Cost | 0 | 23070.207 | 25764 | 0
Year One Bill (Total Utility Cost) | 2303072.32 | 2303072.32 | 2303070 | 2303072.32
MicroGrid Upgrade Costs | 31116.4431 | 0 | 0 | 31119.3223
Total Unserved Load | 0 | 465.5327 | 3205.5056 | 0
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 50
LCC |  |  |  |  | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] |  |  |  |  | Gen_min_turndown_pct | 0
Battery Rated Power [kW] |  |  |  |  | Generator allowed? | YES
Battery Storage Capacity [kWh] |  |  |  |  | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 150
LCC |  |  |  |  | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] |  |  |  |  | Gen_min_turndown_pct | 0
Battery Rated Power [kW] |  |  |  |  | Generator allowed? | YES
Battery Storage Capacity [kWh] |  |  |  |  | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 100
LCC |  |  |  |  | Microgrid_Premium_Pct | 0.15
PV Rated Capacity [kW] |  |  |  |  | Gen_min_turndown_pct | 0
Battery Rated Power [kW] |  |  |  |  | Generator allowed? | YES
Battery Storage Capacity [kWh] |  |  |  |  | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 100
LCC |  |  |  |  | Microgrid_Premium_Pct | 0.5
PV Rated Capacity [kW] |  |  |  |  | Gen_min_turndown_pct | 0
Battery Rated Power [kW] |  |  |  |  | Generator allowed? | YES
Battery Storage Capacity [kWh] |  |  |  |  | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load
STM EXISTING PV SSEB CRIT | # Outage Start Timesteps |  |  |  | INPUT ASSUMPTIONS
2 HOUR OUTAGE DURATION | 12 | 52 | 365 | 8760 | VoLL | 100
LCC |  |  |  |  | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] |  |  |  |  | Gen_min_turndown_pct | 0.25
Battery Rated Power [kW] |  |  |  |  | Generator allowed? | YES
Battery Storage Capacity [kWh] |  |  |  |  | Generator_existing_kw | 0
Generator Rated Power [kW]
Net Capital Cost (plus O&M)
Expected Outage Cost
Max Outage Cost
Year One Bill (Total Utility Cost)
MicroGrid Upgrade Costs
Total Unserved Load

## JuMP Model Results
STM EXISTING PV | VoLL ($/kWh) |  | INPUT ASSUMPTIONS | 100% Renewable | STM WITH EXISTING PV | STM Baseline | 1 Hr | 3 Hr | 10 Hr | 24 Hr
2-WEEK OUTAGE DURATION | 0 (Grid-Optimal) | 40 (Cost-Robust) | Outage_start_timesteps | 26 | NPV | 406512 | -1951517 | -2618918 | -11295829 | -29634101
LCC | 55739772 | 56829991 | Microgrid_Premium_Pct | Default (0.30) | PV Rated Capacity [kW] | 3830.7049 | 3776.5918 | 3907.4017 | 4289.3379 | 7505.7646
PV Rated Capacity [kW] | 3832.896 | 3807.3939 | Gen_min_turndown_pct | 0 | Battery Storage Capacity [kWh] | 675.6722 | 1887.399 | 1879.9992 | 17951.7657 | 42079.4774
Microgrid PV Rated Capacity [kW] | 0 | 16.1 | Generator allowed? | NO | Battery Rated Power [kW] | 325.5633 | 1013.8258 | 622.4096 | 1846.7016 | 4112.2006
Battery Rated Power [kW] | 338.931 | 546.222 | Generator_existing_kw | n/a | Generator Rated Power [kW] | 0 | 1135.01 | 1804.44 | 867.763 | 433.553
Battery Storage Capacity [kWh] | 732.073 | 1984.9 | Critical Load | 100% SSEB Gross Load | Initial Capital Cost | 957519.34 | 2525509.13 | 2737622.45 | 10658929.08 | 27624764.87
Generator Rated Power [kW] | 0 | 0 | MG PV constrained? | Yes (16.1 kW) | Net Capital Cost (plus O&M) | 2915736 | 6455919 | 7239810 | 20856749 | 50430082
Net Capital Cost (plus O&M) | 2984475 | 4177807 |  |  | Energy Savings (Year One) | 12028 | 9175.84 | 15508.06 | 30487.75 | 178221.01
Max Outage Cost | 0 | 0 |  |  | Demand Savings (Year One) | 78655.81 | 133115.09 | 131868.25 | 332546.38 | 675281.67
Year One Bill (Total Utility Cost) | 2303072.32 | 2267633.73
MicroGrid Upgrade Costs | 0 | 709849.99
Unserved Load Remaining [kWh] | 3205.924 | 0
NPV | 403526.85 | 2247378.31
Demand Savings | 81527.73 | 118335.29
Energy Savings | 11996.11 | 10627.13
Outage Savings | 0 | 2934070.46
Utility Bill Savings | 93523.83 | 128962.42
PV Upfront Cost | 403769.6 | 362966.24
Storage Upfront Cost | 592172.7 | 1292484.48
STM EXISTING PV | VoLL ($/kWh) |  | INPUT ASSUMPTIONS | 100% Renewable
2-WEEK OUTAGE DURATION | 0 (Grid-Optimal) | 10 (Cost-Robust) | Outage_start_timesteps | 26
LCC | 55739772 | 59900600 | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | 3832.896 | 3886.424 | Gen_min_turndown_pct | 0
Microgrid PV Rated Capacity [kW] | 0 | 45.06 | Generator allowed? | NO
Battery Rated Power [kW] | 338.931 | 226.4194 | Generator_existing_kw | n/a
Battery Storage Capacity [kWh] | 732.073 | 355.0887 | Critical Load | 50% STM Net Load
Generator Rated Power [kW] | 0 | 0 | MG PV constrained? | No (MG PV = 45.06 kW)
Net Capital Cost (plus O&M) | 2984475 | 2671343
Max Outage Cost | 0 | 0
Year One Bill (Total Utility Cost) | 2303072.32 | 2318271.4
MicroGrid Upgrade Costs | 0 | 214900.6649
Unserved Load Remaining [kWh] | 729134.75 | 0
NPV | 403526.85 | 886756.4678
Demand Savings | 81527.73 | 63701.98
Energy Savings | 11996.11 | 14622.76
Outage Savings | 0 | 733517.6147
Utility Bill Savings | 93523.83 | 78324.75
PV Upfront Cost | 403769.6 | 489414.4
Storage Upfront Cost | 592172.7 | 339329.5649
STM EXISTING PV | VoLL ($/kWh) |  | INPUT ASSUMPTIONS | 100% Renewable
2-WEEK OUTAGE DURATION | 0 (Grid-Optimal) | 60 (Cost-Robust) | Outage_start_timesteps | 26
LCC | 55739772 | 198970668 | Microgrid_Premium_Pct | Default (0.30)
PV Rated Capacity [kW] | 3832.896 | 20509.996 | Gen_min_turndown_pct | 0
Battery Rated Power [kW] | 338.931 | 5545.73 | Generator allowed? | NO
Battery Storage Capacity [kWh] | 732.073 | 112310.42 | Generator_existing_kw | n/a
Generator Rated Power [kW] | 0 | 0 | Critical Load | 50% STM Net Load
Net Capital Cost (plus O&M) | 2984475 | 139582833
Max Outage Cost | 0 | 0
Year One Bill (Total Utility Cost) | 2303072.32 | 752732.08
MicroGrid Upgrade Costs | 0 | 42221556.3047
Unserved Load Remaining [kWh] | 729134.75 | 0
NPV | 403526.85 | 859300819.58
Demand Savings | 81527.73 | 950554.21
Energy Savings | 11996.11 | 693309.85
Outage Savings | 0 | 1002128189.12
Utility Bill Savings | 93523.83 | 1643864.07
PV Upfront Cost | 403769.6 | 27087129.6
Storage Upfront Cost | 592172.7 | 51828789.6